## data
Quarter | Year | Brand name | Brand logo | Region | Unit photo | Unit name | Unit type | Execution | Unit size quantity | Eurovent Certificate | Casing Strength (Eurovent) | Casing leakage, negative pressure (Eurovent) | Casing leakage, positive pressure (Eurovent) | Filter mounting leakage (Eurovent) | Thermal isolation (Eurovent) | Thermal bridges (Eurovent) | VDI 6022-1 certification | Supply | Exhaust | Supply/Exhaust without recovery | Supply/Exhaust with RRG | Supply/Exhaust with PCR (HEX) | Supply/Exhaust with glycol | Insulation material | Insulation thickness [mm] | Metal sheet (Internal) | Metal sheet thickness (Internal) [mm] | Metal sheet (External) | Metal sheet thickness (External) [mm] | Unit size | Recovery type | Minimum airflow [CMH] | Maximum airflow (CCOL) [CMH] | Optimal airflow (ErP2018) [CMH] | Air speed on Filter at opt airflow (ErP) [m/s] | Internal Width (Supply Filter) [mm] | Internal Height (Supply Filter) [mm] | Unit cross section area (Supply Filter) [m2] | Internal Width (Supply Fan) [mm] | Internal Height (Supply Fan) [mm] | x1 | x2 | x3 | x4 | x5 | y1 | y2 | y3 | y4 | y5 | x6 | x7 | x8 | x9 | x10 | y6 | y7 | y8 | y9 | y10 | Unit cross section area (Supply Fan) [m2] | Duct connection Width [mm] | Duct connection Height [mm] | x11 | x12 | x13 | x14 | x15 | y11 | y12 | y13 | y14 | y15 | Duct connection Diameter [mm] | Type | Wheel diameter [mm] | Distance between lamels [mm] | Sens. efficiency at nominal balanced airflows [%] | Sens. efficiency at opt balanced airflows (ErP) [%] | Material | Sens. efficiency at nominal balanced airflows [%] | Sens. efficiency at opt balanced airflows (ErP) [%] | Motor type | Motor quantity | Motor rated power [kW] | Impeller size | Impeller efficiency at nominal airflow [%] | Heating elements type | Capacity range1 [kW] | Capacity range2 [kW] | Capacity range3 [kW] | Water heater_min rows | Water heater_max rows | Water cooler_min rows | Water cooler_max rows | DXH_min rows | DXH_max rows | DXH sections range | Available refrigerant types | Filter type_Supply | Filtration class_Supply | Filtration efficiency_Supply | Initial PD at nominal airflow_Supply | Final PD_Supply | Filter type_Exhaust | Filtration class_Exhaust | Filtration efficiency_Exhaust | Initial PD at nominal airflow_Exhaust | Final PD_Exhaust | Silencer casing
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR20 | RRG | 421 | 2185 | 1740 | 2.1 | 650 | 418.5 | 0.27203 | 650 | 418.5 | 0 | 0 | 650 | 650 | 0 | 0 | 418.5 | 418.5 | 0 | 0 | 0 | 0 | 650 | 650 | 0 | 0 | 418.5 | 418.5 | 0 | 0 | 0.27203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | NH.RRG | 590 | 1.4 | N/A | 76.5 | 0 | 0 | 0 | EC | 1 | 0.78 | N/A | N/A | Tubular | 5.2 | 0 | 0 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 143 | 353 | Bag | ePM10 | 60 | 99 | 297 | NO
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR20 | RRG | 421 | 2185 | 1650 | 2 | 650 | 418.5 | 0.27203 | 650 | 418.5 | 0 | 0 | 650 | 650 | 0 | 0 | 418.5 | 418.5 | 0 | 0 | 0 | 0 | 650 | 650 | 0 | 0 | 418.5 | 418.5 | 0 | 0 | 0.27203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | Total | 590 | 1.4 | N/A | 75.1 | 0 | 0 | 0 | EC | 1 | 0.78 | N/A | N/A | Tubular | 5.2 | 0 | 0 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 143 | 353 | Bag | ePM10 | 60 | 99 | 297 | NO
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 7 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SC20 | HEX | 421 | 2185 | 1740 | 2.1 | 650 | 418.5 | 0.27203 | 650 | 418.5 | 0 | 0 | 650 | 650 | 0 | 0 | 418.5 | 418.5 | 0 | 0 | 0 | 0 | 650 | 650 | 0 | 0 | 418.5 | 418.5 | 0 | 0 | 0.27203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | N/A | 0 | AL | N/A | 86.5 | EC | 1 | 0.78 | N/A | N/A | Tubular | 5.2 | 0 | 0 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 143 | 353 | Bag | ePM10 | 60 | 99 | 297 | NO
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR25 | RRG | 590 | 2614 | 2050 | 1.9 | 765 | 468.5 | 0.3584 | 765 | 468.5 | 0 | 0 | 765 | 765 | 0 | 0 | 468.5 | 468.5 | 0 | 0 | 0 | 0 | 765 | 765 | 0 | 0 | 468.5 | 468.5 | 0 | 0 | 0.3584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | NH.RRG | 700 | 1.4 | N/A | 78.5 | 0 | 0 | 0 | EC | 1 | 0.78 | N/A | N/A | Tubular | 5.2 | 0 | 0 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 100 | 273 | Bag | ePM10 | 60 | 64 | 191 | NO
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR25 | RRG | 590 | 2614 | 2050 | 1.9 | 765 | 780 | 0.5967 | 466 | 780 | 0 | 0 | 780 | 780 | 0 | 0 | 466 | 466 | 0 | 0 | 0 | 0 | 780 | 780 | 0 | 0 | 466 | 466 | 0 | 0 | 0.5967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | Total | 700 | 1.4 | N/A | 76.9 | 0 | 0 | 0 | EC | 1 | 0.78 | N/A | N/A | Tubular | 5.2 | 0 | 0 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 100 | 273 | Bag | ePM10 | 60 | 64 | 191 | NO
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 7 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SC25 | HEX | 590 | 2614 | 2000 | 1.9 | 765 | 780 | 0.5967 | 466 | 780 | 0 | 0 | 780 | 780 | 0 | 0 | 466 | 466 | 0 | 0 | 0 | 0 | 780 | 780 | 0 | 0 | 466 | 466 | 0 | 0 | 0.5967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | N/A | 0 | AL | N/A | 87.1 | EC | 1 | 0.78 | N/A | N/A | Tubular | 5.2 | 0 | 0 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 100 | 273 | Bag | ePM10 | 60 | 64 | 191 | NO
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR35 | RRG | 760 | 4097 | 3100 | 2.2 | 858 | 525.5 | 0.45088 | 858 | 525.5 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0.45088 | 500 | 400 | 0 | 0 | 500 | 500 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | NH.RRG | 793 | 1.4 | N/A | 76.4 | 0 | 0 | 0 | EC | 1 | 1.3 | N/A | N/A | Tubular | 3.5 | 7.1 | 0 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 82 | 246 | Bag | ePM10 | 60 | 58 | 173 | NO
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR35 | RRG | 760 | 4097 | 3100 | 2.2 | 858 | 525.5 | 0.45088 | 858 | 525.5 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0.45088 | 500 | 400 | 0 | 0 | 500 | 500 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Total | 793 | 1.4 | N/A | 74.1 | 0 | 0 | 0 | EC | 1 | 1.3 | N/A | N/A | Tubular | 3.5 | 7.1 | 0 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 82 | 246 | Bag | ePM10 | 60 | 58 | 173 | NO
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 7 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SC35 | HEX | 760 | 4097 | 3100 | 2.2 | 858 | 525.5 | 0.45088 | 858 | 525.5 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0.45088 | 500 | 400 | 0 | 0 | 500 | 500 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | AL | N/A | 88.1 | EC | 1 | 1.3 | N/A | N/A | Tubular | 3.5 | 7.1 | 0 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 82 | 246 | Bag | ePM10 | 60 | 58 | 173 | NO
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR50 | RRG | 1102 | 4968 | 3700 | 2 | 1028 | 602.5 | 0.61937 | 1028 | 602.5 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0.61937 | 700 | 400 | 0 | 0 | 700 | 700 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | NH.RRG | 950 | 1.4 | N/A | 78.8 | 0 | 0 | 0 | EC | 1 | 1.35 | N/A | N/A | Tubular | 3.5 | 7.1 | 10.4 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 79 | 226 | Bag | ePM10 | 60 | 41 | 123 | NO
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR50 | RRG | 1102 | 4968 | 3700 | 2 | 1028 | 602.5 | 0.61937 | 1028 | 602.5 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0.61937 | 700 | 400 | 0 | 0 | 700 | 700 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Total | 950 | 1.4 | N/A | 77.2 | 0 | 0 | 0 | EC | 1 | 1.35 | N/A | N/A | Tubular | 3.5 | 7.1 | 10.4 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 79 | 226 | Bag | ePM10 | 60 | 41 | 123 | NO
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 7 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SC50 | HEX | 1102 | 4968 | 3600 | 1.6 | 1028 | 602.5 | 0.61937 | 1028 | 602.5 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0.61937 | 700 | 400 | 0 | 0 | 700 | 700 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | AL | N/A | 88.4 | EC | 1 | 1.35 | N/A | N/A | Tubular | 3.5 | 7.1 | 10.4 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 79 | 226 | Bag | ePM10 | 60 | 41 | 123 | NO
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR70 | RRG | 1480 | 6862 | 6300 | 1.8 | 1186 | 677 | 0.80292 | 1186 | 677 | 0 | 0 | 1186 | 1186 | 0 | 0 | 677 | 677 | 0 | 0 | 0 | 0 | 1186 | 1186 | 0 | 0 | 677 | 677 | 0 | 0 | 0.80292 | 800 | 400 | 0 | 0 | 800 | 800 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | NH.RRG | 1100 | 1.4 | N/A | 79.6 | 0 | 0 | 0 | EC | 1 | 2.1 | N/A | N/A | Tubular | 3.5 | 10.4 | 14.2 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 70 | 194 | Bag | ePM10 | 60 | 28 | 85 | NO
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR70 | RRG | 1480 | 6862 | 6300 | 1.8 | 1186 | 677 | 0.80292 | 1186 | 677 | 0 | 0 | 1186 | 1186 | 0 | 0 | 677 | 677 | 0 | 0 | 0 | 0 | 1186 | 1186 | 0 | 0 | 677 | 677 | 0 | 0 | 0.80292 | 800 | 400 | 0 | 0 | 800 | 800 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Total | 1100 | 1.4 | N/A | 73 | 0 | 0 | 0 | EC | 1 | 2.1 | N/A | N/A | Tubular | 3.5 | 10.4 | 14.2 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 70 | 194 | Bag | ePM10 | 60 | 28 | 85 | NO
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 7 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SC70 | HEX | 1480 | 6862 | 5400 | 1.7 | 1186 | 677 | 0.80292 | 1186 | 677 | 0 | 0 | 1186 | 1186 | 0 | 0 | 677 | 677 | 0 | 0 | 0 | 0 | 1186 | 1186 | 0 | 0 | 677 | 677 | 0 | 0 | 0.80292 | 800 | 400 | 0 | 0 | 800 | 800 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | AL | N/A | 88.2 | EC | 1 | 2.1 | N/A | N/A | Tubular | 3.5 | 10.4 | 14.2 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 70 | 194 | Bag | ePM10 | 60 | 28 | 85 | NO
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR15 | RRG | 421 | 1429 | 1100 | 1.3 | 650 | 418.5 | 0.27203 | 650 | 418.5 | 0 | 0 | 650 | 650 | 0 | 0 | 418.5 | 418.5 | 0 | 0 | 0 | 0 | 650 | 650 | 0 | 0 | 418.5 | 418.5 | 0 | 0 | 0.27203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | NH.RRG | 590 | 1.4 | N/A | 80.9 | 0 | 0 | 0 | EC | 1 | 0.36 | N/A | N/A | Tubular | 5.2 | 0 | 0 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 70 | 173 | Bag | ePM10 | 60 | 48 | 145 | NO
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR15 | RRG | 421 | 1429 | 1100 | 1.3 | 650 | 418.5 | 0.27203 | 650 | 418.5 | 0 | 0 | 650 | 650 | 0 | 0 | 418.5 | 418.5 | 0 | 0 | 0 | 0 | 650 | 650 | 0 | 0 | 418.5 | 418.5 | 0 | 0 | 0.27203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | Total | 590 | 1.4 | N/A | 80.5 | 0 | 0 | 0 | EC | 1 | 0.36 | N/A | N/A | Tubular | 5.2 | 0 | 0 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 70 | 173 | Bag | ePM10 | 60 | 48 | 145 | NO
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR30 | RRG | 760 | 3125 | 2350 | 1.7 | 858 | 525.5 | 0.45088 | 858 | 525.5 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0.45088 | 500 | 400 | 0 | 0 | 500 | 500 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | NH.RRG | 793 | 1.4 | N/A | 79.6 | 0 | 0 | 0 | EC | 1 | 0.78 | N/A | N/A | Tubular | 3.5 | 7.1 | 0 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 53 | 160 | Bag | ePM10 | 60 | 37 | 112 | NO
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR30 | RRG | 760 | 3125 | 2350 | 1.7 | 858 | 525.5 | 0.45088 | 858 | 525.5 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0.45088 | 500 | 400 | 0 | 0 | 500 | 500 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Total | 793 | 1.4 | N/A | 78.5 | 0 | 0 | 0 | EC | 1 | 0.78 | N/A | N/A | Tubular | 3.5 | 7.1 | 0 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 53 | 160 | Bag | ePM10 | 60 | 37 | 112 | NO
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR60 | RRG | 1102 | 6235 | 4545 | 2.4 | 1028 | 602.5 | 0.61937 | 1028 | 602.5 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0.61937 | 700 | 400 | 0 | 0 | 700 | 700 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | NH.RRG | 950 | 1.4 | N/A | 76.6 | 0 | 0 | 0 | EC | 1 | 2.1 | N/A | N/A | Tubular | 3.5 | 10.4 | 14.2 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 110 | 313 | Bag | ePM10 | 60 | 57 | 171 | NO
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR60 | RRG | 1102 | 6235 | 4545 | 2.4 | 1028 | 602.5 | 0.61937 | 1028 | 602.5 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0.61937 | 700 | 400 | 0 | 0 | 700 | 700 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Total | 950 | 1.4 | N/A | 74.2 | 0 | 0 | 0 | EC | 1 | 2.1 | N/A | N/A | Tubular | 3.5 | 10.4 | 14.2 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 110 | 313 | Bag | ePM10 | 60 | 57 | 171 | NO
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR80 | RRG | 2070 | 7538 | 6200 | 1.8 | 1386 | 777.5 | 1.0776 | 1386 | 777.5 | 0 | 0 | 1386 | 1386 | 0 | 0 | 777.5 | 777.5 | 0 | 0 | 0 | 0 | 1386 | 1386 | 0 | 0 | 777.5 | 777.5 | 0 | 0 | 1.0776 | 1000 | 500 | 0 | 0 | 1000 | 1000 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | NH.RRG | 1300 | 1.4 | N/A | 79.9 | 0 | 0 | 0 | EC | 1 | 2.1 | N/A | N/A | Tubular | 5.2 | 12.3 | 0 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 67 | 190 | Bag | ePM10 | 60 | 39 | 118 | NO
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR80 | RRG | 2070 | 7538 | 6200 | 1.8 | 1386 | 777.5 | 1.0776 | 1386 | 777.5 | 0 | 0 | 1386 | 1386 | 0 | 0 | 777.5 | 777.5 | 0 | 0 | 0 | 0 | 1386 | 1386 | 0 | 0 | 777.5 | 777.5 | 0 | 0 | 1.0776 | 1000 | 500 | 0 | 0 | 1000 | 1000 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | Total | 1300 | 1.4 | N/A | 78.7 | 0 | 0 | 0 | EC | 1 | 2.1 | N/A | N/A | Tubular | 5.2 | 12.3 | 0 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 67 | 190 | Bag | ePM10 | 60 | 39 | 118 | NO
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 7 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SC30 | HEX | 760 | 3125 | 2350 | 1.7 | 858 | 525.5 | 0.45088 | 858 | 525.5 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0.45088 | 500 | 400 | 0 | 0 | 500 | 500 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | AL | N/A | 88.8 | EC | 1 | 2.1 | N/A | N/A | Tubular | 3.5 | 10.4 | 14.2 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 70 | 194 | Bag | ePM10 | 60 | 28 | 85 | NO
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 7 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SC60 | HEX | 1102 | 6235 | 4450 | 2 | 1028 | 602.5 | 0.61937 | 1028 | 602.5 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0.61937 | 700 | 400 | 0 | 0 | 700 | 700 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | AL | N/A | 87.7 | EC | 1 | 2.1 | N/A | N/A | Tubular | 3.5 | 10.4 | 14.2 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 70 | 194 | Bag | ePM10 | 60 | 28 | 85 | NO
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR20 | RRG | 421 | 2185 | 1740 | 2.1 | 650 | 418.5 | 0.27203 | 650 | 418.5 | 0 | 0 | 650 | 650 | 0 | 0 | 418.5 | 418.5 | 0 | 0 | 0 | 0 | 650 | 650 | 0 | 0 | 418.5 | 418.5 | 0 | 0 | 0.27203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | NH.RRG | 590 | 1.4 | N/A | 76.5 | 0 | 0 | 0 | EC | 1 | 0.78 | N/A | N/A | Tubular | 5.2 | 0 | 0 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 143 | 353 | Bag | ePM10 | 60 | 99 | 297 | NO
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR20 | RRG | 421 | 2185 | 1650 | 2 | 650 | 418.5 | 0.27203 | 650 | 418.5 | 0 | 0 | 650 | 650 | 0 | 0 | 418.5 | 418.5 | 0 | 0 | 0 | 0 | 650 | 650 | 0 | 0 | 418.5 | 418.5 | 0 | 0 | 0.27203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | Total | 590 | 1.4 | N/A | 75.1 | 0 | 0 | 0 | EC | 1 | 0.78 | N/A | N/A | Tubular | 5.2 | 0 | 0 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 143 | 353 | Bag | ePM10 | 60 | 99 | 297 | NO
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 7 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SC20 | HEX | 421 | 2185 | 1740 | 2.1 | 650 | 418.5 | 0.27203 | 650 | 418.5 | 0 | 0 | 650 | 650 | 0 | 0 | 418.5 | 418.5 | 0 | 0 | 0 | 0 | 650 | 650 | 0 | 0 | 418.5 | 418.5 | 0 | 0 | 0.27203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | N/A | 0 | AL | N/A | 86.5 | EC | 1 | 0.78 | N/A | N/A | Tubular | 5.2 | 0 | 0 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 143 | 353 | Bag | ePM10 | 60 | 99 | 297 | NO
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR25 | RRG | 590 | 2614 | 2050 | 1.9 | 765 | 468.5 | 0.3584 | 765 | 468.5 | 0 | 0 | 765 | 765 | 0 | 0 | 468.5 | 468.5 | 0 | 0 | 0 | 0 | 765 | 765 | 0 | 0 | 468.5 | 468.5 | 0 | 0 | 0.3584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | NH.RRG | 700 | 1.4 | N/A | 78.5 | 0 | 0 | 0 | EC | 1 | 0.78 | N/A | N/A | Tubular | 5.2 | 0 | 0 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 100 | 273 | Bag | ePM10 | 60 | 64 | 191 | NO
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR25 | RRG | 590 | 2614 | 2050 | 1.9 | 765 | 780 | 0.5967 | 466 | 780 | 0 | 0 | 780 | 780 | 0 | 0 | 466 | 466 | 0 | 0 | 0 | 0 | 780 | 780 | 0 | 0 | 466 | 466 | 0 | 0 | 0.5967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | Total | 700 | 1.4 | N/A | 76.9 | 0 | 0 | 0 | EC | 1 | 0.78 | N/A | N/A | Tubular | 5.2 | 0 | 0 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 100 | 273 | Bag | ePM10 | 60 | 64 | 191 | NO
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 7 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SC25 | HEX | 590 | 2614 | 2000 | 1.9 | 765 | 780 | 0.5967 | 466 | 780 | 0 | 0 | 780 | 780 | 0 | 0 | 466 | 466 | 0 | 0 | 0 | 0 | 780 | 780 | 0 | 0 | 466 | 466 | 0 | 0 | 0.5967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | N/A | 0 | AL | N/A | 87.1 | EC | 1 | 0.78 | N/A | N/A | Tubular | 5.2 | 0 | 0 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 100 | 273 | Bag | ePM10 | 60 | 64 | 191 | NO
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR35 | RRG | 760 | 4097 | 3100 | 2.2 | 858 | 525.5 | 0.45088 | 858 | 525.5 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0.45088 | 500 | 400 | 0 | 0 | 500 | 500 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | NH.RRG | 793 | 1.4 | N/A | 76.4 | 0 | 0 | 0 | EC | 1 | 1.3 | N/A | N/A | Tubular | 3.5 | 7.1 | 0 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 82 | 246 | Bag | ePM10 | 60 | 58 | 173 | NO
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR35 | RRG | 760 | 4097 | 3100 | 2.2 | 858 | 525.5 | 0.45088 | 858 | 525.5 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0.45088 | 500 | 400 | 0 | 0 | 500 | 500 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Total | 793 | 1.4 | N/A | 74.1 | 0 | 0 | 0 | EC | 1 | 1.3 | N/A | N/A | Tubular | 3.5 | 7.1 | 0 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 82 | 246 | Bag | ePM10 | 60 | 58 | 173 | NO
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 7 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SC35 | HEX | 760 | 4097 | 3100 | 2.2 | 858 | 525.5 | 0.45088 | 858 | 525.5 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0.45088 | 500 | 400 | 0 | 0 | 500 | 500 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | AL | N/A | 88.1 | EC | 1 | 1.3 | N/A | N/A | Tubular | 3.5 | 7.1 | 0 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 82 | 246 | Bag | ePM10 | 60 | 58 | 173 | NO
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR50 | RRG | 1102 | 4968 | 3700 | 2 | 1028 | 602.5 | 0.61937 | 1028 | 602.5 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0.61937 | 700 | 400 | 0 | 0 | 700 | 700 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | NH.RRG | 950 | 1.4 | N/A | 78.8 | 0 | 0 | 0 | EC | 1 | 1.35 | N/A | N/A | Tubular | 3.5 | 7.1 | 10.4 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 79 | 226 | Bag | ePM10 | 60 | 41 | 123 | NO
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR50 | RRG | 1102 | 4968 | 3700 | 2 | 1028 | 602.5 | 0.61937 | 1028 | 602.5 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0.61937 | 700 | 400 | 0 | 0 | 700 | 700 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Total | 950 | 1.4 | N/A | 77.2 | 0 | 0 | 0 | EC | 1 | 1.35 | N/A | N/A | Tubular | 3.5 | 7.1 | 10.4 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 79 | 226 | Bag | ePM10 | 60 | 41 | 123 | NO
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 7 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SC50 | HEX | 1102 | 4968 | 3600 | 1.6 | 1028 | 602.5 | 0.61937 | 1028 | 602.5 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0.61937 | 700 | 400 | 0 | 0 | 700 | 700 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | AL | N/A | 88.4 | EC | 1 | 1.35 | N/A | N/A | Tubular | 3.5 | 7.1 | 10.4 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 79 | 226 | Bag | ePM10 | 60 | 41 | 123 | NO
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR70 | RRG | 1480 | 6862 | 6300 | 1.8 | 1186 | 677 | 0.80292 | 1186 | 677 | 0 | 0 | 1186 | 1186 | 0 | 0 | 677 | 677 | 0 | 0 | 0 | 0 | 1186 | 1186 | 0 | 0 | 677 | 677 | 0 | 0 | 0.80292 | 800 | 400 | 0 | 0 | 800 | 800 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | NH.RRG | 1100 | 1.4 | N/A | 79.6 | 0 | 0 | 0 | EC | 1 | 2.1 | N/A | N/A | Tubular | 3.5 | 10.4 | 14.2 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 70 | 194 | Bag | ePM10 | 60 | 28 | 85 | NO
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR70 | RRG | 1480 | 6862 | 6300 | 1.8 | 1186 | 677 | 0.80292 | 1186 | 677 | 0 | 0 | 1186 | 1186 | 0 | 0 | 677 | 677 | 0 | 0 | 0 | 0 | 1186 | 1186 | 0 | 0 | 677 | 677 | 0 | 0 | 0.80292 | 800 | 400 | 0 | 0 | 800 | 800 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Total | 1100 | 1.4 | N/A | 73 | 0 | 0 | 0 | EC | 1 | 2.1 | N/A | N/A | Tubular | 3.5 | 10.4 | 14.2 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 70 | 194 | Bag | ePM10 | 60 | 28 | 85 | NO
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 7 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SC70 | HEX | 1480 | 6862 | 5400 | 1.7 | 1186 | 677 | 0.80292 | 1186 | 677 | 0 | 0 | 1186 | 1186 | 0 | 0 | 677 | 677 | 0 | 0 | 0 | 0 | 1186 | 1186 | 0 | 0 | 677 | 677 | 0 | 0 | 0.80292 | 800 | 400 | 0 | 0 | 800 | 800 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | AL | N/A | 88.2 | EC | 1 | 2.1 | N/A | N/A | Tubular | 3.5 | 10.4 | 14.2 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 70 | 194 | Bag | ePM10 | 60 | 28 | 85 | NO
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR15 | RRG | 421 | 1429 | 1100 | 1.3 | 650 | 418.5 | 0.27203 | 650 | 418.5 | 0 | 0 | 650 | 650 | 0 | 0 | 418.5 | 418.5 | 0 | 0 | 0 | 0 | 650 | 650 | 0 | 0 | 418.5 | 418.5 | 0 | 0 | 0.27203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | NH.RRG | 590 | 1.4 | N/A | 80.9 | 0 | 0 | 0 | EC | 1 | 0.36 | N/A | N/A | Tubular | 5.2 | 0 | 0 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 70 | 173 | Bag | ePM10 | 60 | 48 | 145 | NO
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR15 | RRG | 421 | 1429 | 1100 | 1.3 | 650 | 418.5 | 0.27203 | 650 | 418.5 | 0 | 0 | 650 | 650 | 0 | 0 | 418.5 | 418.5 | 0 | 0 | 0 | 0 | 650 | 650 | 0 | 0 | 418.5 | 418.5 | 0 | 0 | 0.27203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | Total | 590 | 1.4 | N/A | 80.5 | 0 | 0 | 0 | EC | 1 | 0.36 | N/A | N/A | Tubular | 5.2 | 0 | 0 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 70 | 173 | Bag | ePM10 | 60 | 48 | 145 | NO
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR30 | RRG | 760 | 3125 | 2350 | 1.7 | 858 | 525.5 | 0.45088 | 858 | 525.5 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0.45088 | 500 | 400 | 0 | 0 | 500 | 500 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | NH.RRG | 793 | 1.4 | N/A | 79.6 | 0 | 0 | 0 | EC | 1 | 0.78 | N/A | N/A | Tubular | 3.5 | 7.1 | 0 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 53 | 160 | Bag | ePM10 | 60 | 37 | 112 | NO
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR30 | RRG | 760 | 3125 | 2350 | 1.7 | 858 | 525.5 | 0.45088 | 858 | 525.5 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0.45088 | 500 | 400 | 0 | 0 | 500 | 500 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Total | 793 | 1.4 | N/A | 78.5 | 0 | 0 | 0 | EC | 1 | 0.78 | N/A | N/A | Tubular | 3.5 | 7.1 | 0 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 53 | 160 | Bag | ePM10 | 60 | 37 | 112 | NO
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR60 | RRG | 1102 | 6235 | 4545 | 2.4 | 1028 | 602.5 | 0.61937 | 1028 | 602.5 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0.61937 | 700 | 400 | 0 | 0 | 700 | 700 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | NH.RRG | 950 | 1.4 | N/A | 76.6 | 0 | 0 | 0 | EC | 1 | 2.1 | N/A | N/A | Tubular | 3.5 | 10.4 | 14.2 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 110 | 313 | Bag | ePM10 | 60 | 57 | 171 | NO
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR60 | RRG | 1102 | 6235 | 4545 | 2.4 | 1028 | 602.5 | 0.61937 | 1028 | 602.5 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0.61937 | 700 | 400 | 0 | 0 | 700 | 700 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Total | 950 | 1.4 | N/A | 74.2 | 0 | 0 | 0 | EC | 1 | 2.1 | N/A | N/A | Tubular | 3.5 | 10.4 | 14.2 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 110 | 313 | Bag | ePM10 | 60 | 57 | 171 | NO
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR80 | RRG | 2070 | 7538 | 6200 | 1.8 | 1386 | 777.5 | 1.0776 | 1386 | 777.5 | 0 | 0 | 1386 | 1386 | 0 | 0 | 777.5 | 777.5 | 0 | 0 | 0 | 0 | 1386 | 1386 | 0 | 0 | 777.5 | 777.5 | 0 | 0 | 1.0776 | 1000 | 500 | 0 | 0 | 1000 | 1000 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | NH.RRG | 1300 | 1.4 | N/A | 79.9 | 0 | 0 | 0 | EC | 1 | 2.1 | N/A | N/A | Tubular | 5.2 | 12.3 | 0 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 67 | 190 | Bag | ePM10 | 60 | 39 | 118 | NO
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR80 | RRG | 2070 | 7538 | 6200 | 1.8 | 1386 | 777.5 | 1.0776 | 1386 | 777.5 | 0 | 0 | 1386 | 1386 | 0 | 0 | 777.5 | 777.5 | 0 | 0 | 0 | 0 | 1386 | 1386 | 0 | 0 | 777.5 | 777.5 | 0 | 0 | 1.0776 | 1000 | 500 | 0 | 0 | 1000 | 1000 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | Total | 1300 | 1.4 | N/A | 78.7 | 0 | 0 | 0 | EC | 1 | 2.1 | N/A | N/A | Tubular | 5.2 | 12.3 | 0 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 67 | 190 | Bag | ePM10 | 60 | 39 | 118 | NO
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 7 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SC30 | HEX | 760 | 3125 | 2350 | 1.7 | 858 | 525.5 | 0.45088 | 858 | 525.5 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0.45088 | 500 | 400 | 0 | 0 | 500 | 500 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | AL | N/A | 88.8 | EC | 1 | 2.1 | N/A | N/A | Tubular | 3.5 | 10.4 | 14.2 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 70 | 194 | Bag | ePM10 | 60 | 28 | 85 | NO
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 7 | YES | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SC60 | HEX | 1102 | 6235 | 4450 | 2 | 1028 | 602.5 | 0.61937 | 1028 | 602.5 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0.61937 | 700 | 400 | 0 | 0 | 700 | 700 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | AL | N/A | 87.7 | EC | 1 | 2.1 | N/A | N/A | Tubular | 3.5 | 10.4 | 14.2 | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 70 | 194 | Bag | ePM10 | 60 | 28 | 85 | NO